## 176_19B
S&C Power Fuses - Type SMD-1A (50E thru 100E) and SMD-2B (50E thru 250E) (115 and 138 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (50E thru 100E) and SMD-2B (50E thru 250E) (115 and 138 kV)
Very Slow Speed (TCC 176-1-9) | [9 empty] | Very Slow Speed (TCC 176-1-9)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
9995.88 | 0.053228 | 9995.88 | 0.054195 | 9995.88 | 0.055957 | 9995.88 | 0.060075 | 9973.87 | 0.065979 | 9968.16 | 0.074112 | 9968.16 | 0.079977 | 9973.87 | 0.086108 | 9968.16 | 0.10722
7200.66 | 0.058183 | 8216.73 | 0.057489 | 8249.67 | 0.060015 | 8492.41 | 0.065078 | 8884.24 | 0.070511 | 9017.52 | 0.079885 | 9332.78 | 0.0844 | 9074.51 | 0.094424 | 9053.75 | 0.12037
5772.89 | 0.062401 | 6788.11 | 0.061288 | 6815.32 | 0.065078 | 7894.55 | 0.067599 | 7507.47 | 0.07839 | 7792.22 | 0.089887 | 8180.94 | 0.09464 | 7655.09 | 0.11361 | 7922.72 | 0.14318
4341.3 | 0.069797 | 5355.76 | 0.067599 | 6660.36 | 0.065798 | 7243.99 | 0.071207 | 6015 | 0.094046 | 6830.51 | 0.10184 | 7105.85 | 0.10939 | 6431.86 | 0.14002 | 6968.81 | 0.1705
4251.08 | 0.070428 | 5223.53 | 0.068415 | 6418.43 | 0.066993 | 6707.14 | 0.074708 | 5188.75 | 0.10877 | 5801.84 | 0.12127 | 6161.44 | 0.12879 | 5638.05 | 0.16683 | 6028.79 | 0.21037
4137.84 | 0.071278 | 5008.68 | 0.069797 | 6093.2 | 0.068827 | 6081.02 | 0.079885 | 4506.88 | 0.12717 | 4939.38 | 0.14708 | 5394.82 | 0.15222 | 4925.26 | 0.20153 | 5082.87 | 0.27408
3983.55 | 0.072645 | 4717 | 0.071923 | 5726.89 | 0.071136 | 5574.33 | 0.085421 | 3810.64 | 0.15602 | 4248.7 | 0.17859 | 4750.71 | 0.18065 | 4453 | 0.23428 | 4491.42 | 0.33625
3759.08 | 0.074708 | 4442.3 | 0.074336 | 5350.41 | 0.073965 | 5069.15 | 0.092258 | 3353.75 | 0.18452 | 3627.5 | 0.22392 | 4214.77 | 0.21414 | 3971.06 | 0.28011 | 3896.71 | 0.42669
3518.99 | 0.077369 | 4117.2 | 0.077369 | 4939.05 | 0.077447 | 4674.74 | 0.099444 | 2874.9 | 0.2299 | 3104.22 | 0.28334 | 3726.47 | 0.25794 | 3539.25 | 0.3376 | 3476.97 | 0.5178
3297.53 | 0.080205 | 3831.18 | 0.08093 | 4541.12 | 0.081907 | 4183.6 | 0.11056 | 2512.88 | 0.28107 | 2635.21 | 0.36978 | 3338.42 | 0.30787 | 3125.63 | 0.41679 | 3141.78 | 0.62265
3083.83 | 0.083479 | 3501.44 | 0.085763 | 4217.21 | 0.086366 | 3858.09 | 0.12001 | 2171.43 | 0.35484 | 2230.67 | 0.49151 | 2975.41 | 0.37147 | 2733.6 | 0.52798 | 2830.79 | 0.75301
2849.58 | 0.087671 | 3190.49 | 0.091706 | 3892.97 | 0.091615 | 3579.32 | 0.1304 | 1865.66 | 0.45756 | 1916.56 | 0.64478 | 2618.66 | 0.46257 | 2350.01 | 0.68985 | 2536.01 | 0.92593
2648.98 | 0.092166 | 2907.15 | 0.098553 | 3666.26 | 0.096215 | 3307.43 | 0.14311 | 1671.38 | 0.554 | 1637.27 | 0.86593 | 2316.6 | 0.57271 | 2162.74 | 0.80519 | 2298.1 | 1.1269
2460.03 | 0.097377 | 2635.76 | 0.10697 | 3459.67 | 0.10125 | 2998.68 | 0.16168 | 1498.19 | 0.67771 | 1405.91 | 1.1616 | 2058.8 | 0.71233 | 1930.88 | 0.99577 | 2056.44 | 1.3952
2300.61 | 0.10257 | 2416.14 | 0.116 | 3168.23 | 0.10957 | 2784.79 | 0.17868 | 1340.65 | 0.83286 | 1233.1 | 1.5125 | 1866.72 | 0.85313 | 1680.98 | 1.307 | 1929.77 | 1.5861
2132.24 | 0.10935 | 2170.97 | 0.12923 | 2858.15 | 0.12122 | 2534.95 | 0.2045 | 1141.36 | 1.1217 | 1060.07 | 2.0629 | 1643.85 | 1.0944 | 1511.99 | 1.6201 | 1729.81 | 1.9762
1990.08 | 0.11635 | 2004.05 | 0.14098 | 2586.16 | 0.13531 | 2309.83 | 0.23383 | 991.937 | 1.469 | 921.821 | 2.8024 | 1465.94 | 1.3699 | 1367.79 | 1.9932 | 1557.69 | 2.4778
1806.1 | 0.12756 | 1826.08 | 0.15674 | 2309.83 | 0.15364 | 2100.49 | 0.27113 | 863.063 | 1.9381 | 821.584 | 3.6699 | 1328.42 | 1.6806 | 1240.9 | 2.465 | 1408.33 | 3.1031
1640.78 | 0.14098 | 1699.23 | 0.17065 | 2081.67 | 0.17532 | 1937.06 | 0.30908 | 738.141 | 2.6861 | 711.983 | 5.2461 | 1205.18 | 2.07 | 1130.94 | 3.052 | 1264.57 | 4.022
1471.34 | 0.15895 | 1592.29 | 0.18486 | 1896.81 | 0.19826 | 1777.44 | 0.35695 | 639.672 | 3.6825 | 637.477 | 7.0737 | 1074.13 | 2.6846 | 1019.58 | 3.8817 | 1186 | 4.7323
1333.99 | 0.17922 | 1468.4 | 0.20635 | 1719.74 | 0.22669 | 1629.34 | 0.41389 | 576.353 | 4.7107 | 563.945 | 10.0482 | 983.452 | 3.2973 | 925.524 | 4.9485 | 1071.67 | 6.2364
1224.06 | 0.19946 | 1358.22 | 0.22989 | 1584.35 | 0.25534 | 1492.08 | 0.48183 | 519.896 | 6.1478 | 519.599 | 13.2268 | 886.103 | 4.2082 | 842.068 | 6.3372 | 983.452 | 8.1158
1140.16 | 0.21977 | 1241.32 | 0.26154 | 1447.98 | 0.29254 | 1342.01 | 0.58324 | 464.161 | 8.6088 | 470.585 | 19.7937 | 803.436 | 5.3923 | 776.296 | 7.9593 | 898.367 | 10.8309
1049.35 | 0.24656 | 1160.87 | 0.28963 | 1326.01 | 0.33583 | 1222.83 | 0.69201 | 424.976 | 11.7484 | 440.589 | 26.9351 | 738.141 | 6.7454 | 719.36 | 10.2398 | 833.909 | 14.2001
958.08 | 0.28107 | 1079.15 | 0.32395 | 1193.84 | 0.39845 | 1087.82 | 0.85201 | 396.295 | 15.28 | 418.215 | 36.4229 | 687.145 | 8.1905 | 661.656 | 13.9662 | 782.994 | 18.4265
869.511 | 0.32558 | 992.206 | 0.37003 | 1103.15 | 0.45605 | 991.214 | 1.019 | 369.762 | 20.9123 | 396.75 | 52.4848 | 649.64 | 9.6424 | 617.71 | 18.8642 | 735.609 | 24.325
809.916 | 0.3638 | 912.265 | 0.42521 | 1010.22 | 0.52985 | 904.092 | 1.2175 | 348.381 | 30.4116 | 385.77 | 68.4576 | 609.626 | 11.9999 | 577.344 | 25.8028 | 697.054 | 32.2407
740.948 | 0.41972 | 829.589 | 0.49999 | 922.356 | 0.62054 | 812.35 | 1.5126 | 331.448 | 45.7718 | 374.88 | 98.7029 | 573.389 | 15.0283 | 550.226 | 34.9317 | 669.278 | 42.8303
673.125 | 0.49206 | 767.341 | 0.57112 | 862.583 | 0.70176 | 743.175 | 1.8164 | 319.336 | 69.3652 | 368.283 | 140.851 | 535.919 | 20.1482 | 525.886 | 50.4226 | 646.67 | 57.8177
619.511 | 0.56543 | 699.895 | 0.6729 | 804.267 | 0.80079 | 678.532 | 2.2097 | 311.746 | 99.8969 | 363.672 | 195.661 | 504.641 | 27.183 | 508.122 | 75.4999 | 628.415 | 81.0092
575.898 | 0.64136 | 625.738 | 0.82024 | 748.395 | 0.91836 | 632.026 | 2.575 | 304.337 | 162.622 | 361.181 | 273.203 | 482.594 | 34.8518 | 493.495 | 113.373 | 612.426 | 108.856
527.913 | 0.7474 | 558.878 | 1.015 | 697.799 | 1.0521 | 582.851 | 3.0705 | 301.734 | 223.843 | 359.736 | 341.955 | 463.629 | 46.3521 | 483.424 | 185.939 | 604.066 | 146.192
492.715 | 0.84606 | 510.265 | 1.2066 | 648.026 | 1.2139 | 542.361 | 3.6213 | 299.839 | 331.543 | 358.913 | 470.959 | 448.996 | 64.2419 | 480.113 | 258.887 | 599.585 | 212.6
458.487 | 0.96642 | 468.685 | 1.426 | 606.031 | 1.3866 | 508.737 | 4.2158 | 298.81 | 476.383 | 359.53 | 598.318 | 436.32 | 90.32 | 478.192 | 397.533 | 597.87 | 295.668
420.284 | 1.1409 | 427.063 | 1.7261 | 569.029 | 1.5807 | 475.293 | 4.9671 | 298.468 | 570.22 |  |  | 429.379 | 120.813 | 477.918 | 518.218 | 596.844 | 388.308
384.495 | 1.3523 | 393.441 | 2.0398 | 534.82 | 1.8001 | 443.16 | 5.9408 | 298.639 | 604.517 |  |  | 424.003 | 164.872 | 478.192 | 601.065 | 595.478 | 493.317
349.999 | 1.6272 | 362.104 | 2.4274 | 501.163 | 2.0706 | 416.519 | 7.0487 |  |  |  |  | 421.823 | 214.557 |  |  | 596.161 | 535.718
323.737 | 1.9114 | 332.264 | 2.9325 | 466.814 | 2.4226 | 387.583 | 8.5749 |  |  |  |  | 420.376 | 284.376 |  |  | 596.502 | 603.479
306.106 | 2.1422 | 306.412 | 3.5284 | 442.717 | 2.7206 | 367.209 | 10.0829 |  |  |  |  | 419.655 | 366.908
283.42 | 2.5039 | 284.556 | 4.1948 | 419.025 | 3.0983 | 346.863 | 12.1198 |  |  |  |  | 419.655 | 476.383
260.586 | 3.0037 | 269.328 | 4.7963 | 398.191 | 3.5003 | 328.63 | 14.5537 |  |  |  |  | 421.582 | 579.768
240.07 | 3.6033 | 255.681 | 5.4676 | 379.15 | 3.9426 | 315.113 | 17.1645 |  |  |  |  | 421.34 | 599.346
222.723 | 4.2667 | 244.186 | 6.2516 | 363.555 | 4.3616 | 303.06 | 20.0423
208.498 | 5.0422 | 231.813 | 7.2925 | 348.602 | 4.8639 | 289.146 | 25.3517
195.182 | 5.9349 | 221.391 | 8.4388 | 333.93 | 5.4676 | 277.253 | 31.4955
184.737 | 6.8747 | 212.285 | 9.7361 | 321.157 | 6.1034 | 267.717 | 38.2769
174.501 | 8.0353 | 203.35 | 11.2779 | 304.579 | 7.0628 | 259.805 | 46.6115
168.331 | 8.916 | 195.572 | 13.0507 | 293.222 | 7.8605 | 251.371 | 58.7827
162.216 | 9.9229 | 188.846 | 15.1022 | 282.289 | 8.8273 | 243.698 | 76.161
157.108 | 11.0435 | 182.168 | 17.7049 | 272.307 | 10.0026 | 236.733 | 100.068
151.249 | 12.8564 | 175.903 | 20.8602 | 261.368 | 11.5403 | 231.581 | 128.747
146.633 | 14.7146 | 170.533 | 24.627 | 250.618 | 13.4213 | 227.223 | 166.309
140.18 | 18.0085 | 166.656 | 28.4699 | 243.211 | 15.0871 | 223.84 | 214.831
136.31 | 20.6733 | 162.379 | 34.4272 | 236.969 | 17.0448 | 220.287 | 283.965
131.885 | 24.5533 | 159.641 | 40.2394 | 229.736 | 19.6847 | 216.79 | 386.778
128.243 | 28.987 | 157.108 | 47.5056 | 223.616 | 22.6429 | 214.848 | 502.629
125.202 | 34.1529 | 154.305 | 57.3887 | 217.877 | 26.3073 | 214.419 | 599.954
122.6 | 40.1189 | 152.008 | 69.328 | 213.136 | 30.3212
120.413 | 47.08 | 150.345 | 82.9178 | 208.707 | 35.0525
118.147 | 57.6188 | 148.551 | 104.256 | 204.37 | 40.8884
116.504 | 68.9133 | 146.633 | 130.823 | 200.323 | 47.7437
114.77 | 82.1748 | 144.884 | 181.971 | 196.749 | 56.9315
113.174 | 99.968 | 143.012 | 254.131 | 193.433 | 67.9552
111.936 | 126.83 | 141.873 | 339.289 | 190.172 | 81.2759
110.933 | 172.405 | 140.883 | 471.94 | 186.78 | 100.068
110.38 | 220.489 | 140.321 | 585.141 | 183.999 | 121.007
109.72 | 279.737 | 140.18 | 599.954 | 181.26 | 154.447
109.173 | 342.014 |  |  | 179.098 | 188.83
108.737 | 445.346 |  |  | 176.431 | 239.332
108.628 | 574.128 |  |  | 174.85 | 290.281
108.628 | 599.954 |  |  | 172.592 | 391.448
|  |  |  | 171.388 | 540.153
|  |  |  | 171.046 | 599.954